## VLV32
0.6/1kV-1 core aluminum conductor PVC insulated steel wire armored PVC sheathed power cable
Nominal cross sectional area | Insulation thickness | Non-magnetic steel Wire diameter | Sheath thickness | Approximate outer diameter | Approx. weight | Max.D.C resistance of conductor（20℃） | Current carrying capacity
mm2 | mm | mm | mm | mm | kg/km | Ω/km | In Air(A) | In Ground(A)
1X10 | 1 | 0.8 | 1.8 | 13.8 | 316 | 3.08 | 38.5 | 52.5
1X16 | 1 | 0.8 | 1.8 | 14.9 | 375 | 1.91 | 49.7 | 67.9
1X25 | 1.2 | 0.8 | 1.8 | 16.6 | 454 | 1.2 | 65.8 | 87.5
1X35 | 1.2 | 1.25 | 1.8 | 18.1 | 625 | 0.868 | 80.5 | 105
1X50 | 1.4 | 1.25 | 1.8 | 19.8 | 737 | 0.641 | 98 | 122.5
1X70 | 1.4 | 1.25 | 1.8 | 21.4 | 863 | 0.443 | 126 | 150.5
1X95 | 1.6 | 1.6 | 1.8 | 24.1 | 1164 | 0.32 | 154 | 182
1X120 | 1.6 | 1.6 | 1.8 | 25.5 | 1295 | 0.253 | 182 | 206.5
1X150 | 1.8 | 1.6 | 1.8 | 27.5 | 1494 | 0.206 | 210 | 234.5
1X185 | 2 | 1.6 | 1.8 | 29.6 | 1719 | 0.164 | 245 | 266
1X240 | 2.2 | 1.6 | 1.9 | 32.4 | 2042 | 0.125 | 289.8 | 311.5
1x300 | 2.4 | 2 | 2 | 36 | 2637 | 0.1 | 339.5 | 353.5
1x400 | 2.6 | 2 | 2.2 | 40 | 3177 | 0.0778 | 399 | 402.5
1x500 | 2.8 | 2 | 2.3 | 44.2 | 3787 | 0.0605 | 469 | 465.5
1X630 | 2.8 | 2.5 | 2.4 | 48.9 | 4839 | 0.0469 | 553 | 532
1X800 | 2.8 | 2.5 | 2.6 | 53.2 | 5689 | 0.0367 | 644 | 612.5
0.6/1kV-2 core aluminum conductor PVC insulated steel wire armored PVC sheathed power cable
Nominal cross sectional area | Insulation thickness | Steel Wire diameter | Sheath thickness | Approximate outer diameter | Approx. weight | Max.D.C resistance of conductor（20℃） | Current carrying capacity
mm2 | mm | mm | mm | mm | kg/km | Ω/km | In Air(A) | In Ground(A)
2X2.5 | 0.8 | 0.8 | 1.8 | 15.2 | 356 | 12.1 | 17.5 | 25.2
2X4 | 1 | 0.8 | 1.8 | 17.8 | 552 | 7.41 | 23.8 | 32.9
2X6 | 1 | 1.25 | 1.8 | 18.8 | 605 | 4.61 | 31.5 | 42.7
2X10 | 1 | 1.25 | 1.8 | 21.3 | 746 | 3.08 | 40.6 | 54.6
2X16 | 1 | 1.25 | 1.8 | 23.5 | 895 | 1.91 | 52.5 | 70
2X25 | 1.2 | 1.6 | 1.8 | 27.5 | 1273 | 1.2 | 70 | 91
2X35 | 1.2 | 1.6 | 1.8 | 28.8 | 1416 | 0.868 | 84 | 108.5
2X50 | 1.4 | 1.6 | 1.9 | 32.5 | 1713 | 0.641 | 105 | 129.5
2X70 | 1.4 | 2 | 2 | 36.7 | 2311 | 0.443 | 133 | 157.5
2X95 | 1.6 | 2 | 2.1 | 41.6 | 2858 | 0.32 | 164.5 | 192.5
2X120 | 1.6 | 2 | 2.3 | 44.6 | 3228 | 0.253 | 192.5 | 220.5
2X150 | 1.8 | 2.5 | 2.4 | 49.8 | 4200 | 0.206 | 220.5 | 245
2X185 | 2 | 2.5 | 2.6 | 54.4 | 4875 | 0.164 | 255.5 | 276.5
0.6/1kV-3 core aluminum conductor PVC insulated steel wire armored PVC sheathed power cable
Nominal cross sectional area | Insulation thickness | Steel Wire diameter | Sheath thickness | Approximate outer diameter | Approx. weight | Max.D.C resistance of conductor（20℃） | Current carrying capacity
mm2 | mm | mm | mm | mm | kg/km | Ω/km | In Air(A) | In Ground(A)
3X2.5 | 0.8 | 0.8 | 1.8 | 15.7 | 386 | 12.1 | 15.4 | 21.7
3X4 | 1 | 1.25 | 1.8 | 18.4 | 593 | 7.41 | 20.3 | 28
3X6 | 1 | 1.25 | 1.8 | 19.6 | 666 | 4.61 | 27.3 | 36.4
3X10 | 1 | 1.25 | 1.8 | 22.2 | 833 | 3.08 | 35 | 46.2
3X16 | 1 | 1.6 | 1.8 | 25.3 | 1143 | 1.91 | 45.5 | 59.5
3X25 | 1.2 | 1.6 | 1.8 | 28.9 | 1435 | 1.2 | 60.9 | 77
3X35 | 1.2 | 1.6 | 1.8 | 30.4 | 1615 | 0.868 | 73.5 | 91
3X50 | 1.4 | 2 | 1.9 | 35.2 | 2205 | 0.641 | 91 | 112
3X70 | 1.4 | 2 | 2.1 | 39.3 | 2689 | 0.443 | 115.5 | 136.5
3X95 | 1.6 | 2 | 2.2 | 44.1 | 3297 | 0.32 | 143.5 | 164.5
3X120 | 1.6 | 2 | 2.3 | 48.4 | 4185 | 0.253 | 168 | 185.5
3X150 | 1.8 | 2.5 | 2.5 | 53.2 | 4959 | 0.206 | 189 | 210
3X185 | 2 | 2.5 | 2.7 | 57.8 | 5714 | 0.164 | 220.5 | 238
3X240 | 2.2 | 2.5 | 2.9 | 64.4 | 6943 | 0.125 | 262.5 | 276.5
3X300 | 2.4 | 2.5 | 3.1 | 70.2 | 8077 | 0.1 | 304.5 | 311.5
0.6/1kV-4 core aluminum conductor PVC insulated steel wire armored PVC sheathed power cable
Nominal cross sectional area | Insulation thickness | Steel Wire diameter | Sheath thickness | Approximate outer diameter | Approx. weight | Max.D.C resistance of conductor（20℃） | Current carrying capacity
mm2 | mm | mm | mm | mm | kg/km | Ω/km | In Air(A) | In Ground(A)
4X2.5 | 0.8 | 1.25 | 1.8 | 17.5 | 558 | 12.1 | 15.4 | 21.7
4X4 | 1 | 1.25 | 1.8 | 19.5 | 665 | 7.41 | 20.3 | 28
4X6 | 1 | 1.25 | 1.8 | 20.8 | 750 | 4.61 | 27.3 | 36.4
4X10 | 1 | 1.6 | 1.8 | 24.5 | 1085 | 3.08 | 35 | 46.2
4X16 | 1 | 1.6 | 1.8 | 27.1 | 1312 | 1.91 | 45.5 | 59.5
4X25 | 1.2 | 1.6 | 1.9 | 31.3 | 1655 | 1.2 | 60.9 | 77
4X35 | 1.2 | 1.6 | 2 | 33 | 1874 | 0.868 | 73.5 | 91
4X50 | 1.4 | 1.6 | 2.1 | 37.8 | 2370 | 0.641 | 91 | 112
4X70 | 1.4 | 2 | 2.3 | 42.8 | 3162 | 0.443 | 115.5 | 136.5
4X95 | 1.6 | 2.5 | 2.5 | 49.3 | 4340 | 0.32 | 143.5 | 164.5
4X120 | 1.6 | 2.5 | 2.6 | 53.3 | 5030 | 0.253 | 168 | 185.5
4X150 | 1.8 | 2.5 | 2.7 | 58.2 | 5896 | 0.206 | 189 | 210
4X185 | 2 | 2.5 | 2.9 | 63.8 | 6901 | 0.164 | 220.5 | 238
4X240 | 2.2 | 2.5 | 3.1 | 70.7 | 8315 | 0.125 | 262.5 | 276.5
4X300 | 2.4 | 3.15 | 3.4 | 78.6 | 10695 | 0.1 | 304.5 | 311.5
0.6/1kV-5 core aluminum conductor PVC insulated steel wire armored PVC sheathed power cable
Nominal cross sectional area | Insulation thickness | Steel Wire diameter | Sheath thickness | Approximate outer diameter | Approx. weight | Max.D.C resistance of conductor（20℃） | Current carrying capacity
mm2 | mm | mm | mm | mm | kg/km | Ω/km | In Air(A) | In Ground(A)
5X2.5 | 0.8 | 1.25 | 1.8 | 18.4 | 608 | 12.1 | 15.4 | 21.7
5X4 | 1 | 1.25 | 1.8 | 20.7 | 758 | 7.41 | 20.3 | 28
5X6 | 1 | 1.25 | 1.8 | 22.2 | 856 | 4.61 | 27.3 | 36.4
5X10 | 1 | 1.6 | 1.8 | 26.2 | 1245 | 3.08 | 35 | 46.2
5X16 | 1 | 1.6 | 1.8 | 29.2 | 1471 | 1.91 | 45.5 | 59.5
5X25 | 1.2 | 1.6 | 1.9 | 33.9 | 1910 | 1.2 | 60.9 | 77
5X35 | 1.2 | 2 | 2.1 | 36.7 | 2438 | 0.868 | 73.5 | 91
5X50 | 1.4 | 2 | 2.2 | 42.1 | 3043 | 0.641 | 91 | 112
5X70 | 1.4 | 2.5 | 2.4 | 47.7 | 4132 | 0.443 | 115.5 | 136.5
5X95 | 1.6 | 2.5 | 2.6 | 54.2 | 5133 | 0.32 | 143.5 | 164.5
5X120 | 1.6 | 2.5 | 2.7 | 58.2 | 5885 | 0.253 | 168 | 185.5
5X150 | 1.8 | 2.5 | 2.9 | 64.1 | 6952 | 0.206 | 189 | 210
5X185 | 2 | 2.5 | 3.1 | 69.9 | 8114 | 0.164 | 220.5 | 238
5X240 | 2.2 | 3.15 | 3.4 | 79.1 | 10737 | 0.125 | 262.5 | 276.5
5X300 | 2.4 | 3.15 | 3.6 | 86.7 | 12685 | 0.1 | 304.5 | 311.5
0.6/1kV-3+1 core aluminum conductor PVC insulated steel wire armored PVC sheathed power cable
Nominal cross sectional area | Insulation thickness | Steel Wire diameter | Sheath thickness | Approximate outer diameter | Approx. weight | Max.D.C resistance of conductor（20℃） | Current carrying capacity
mm2 | mm | mm | mm | mm | kg/km | Ω/km | In Air(A) | In Ground(A)
3X4+1X2.5 | 1.0/0.8 | 1.25 | 1.8 | 19 | 640 | 7.41/12.1 | 20.3 | 28
3X6+1X4 | 1.0/1.0 | 1.25 | 1.8 | 20.5 | 730 | 4.61/7.41 | 27.3 | 36.4
3X10+1X6 | 1.0/1.0 | 1.6 | 1.8 | 23.8 | 1018 | 3.08/4.61 | 35 | 46.2
3X16+1X10 | 1.0/1.0 | 1.6 | 1.8 | 26.5 | 1230 | 1.91/3.08 | 45.5 | 59.5
3X25+1X16 | 1.2/1.0 | 1.6 | 1.8 | 30.3 | 1565 | 1.2/1.91 | 60.9 | 77
3X35+1X16 | 1.2/1.0 | 1.6 | 1.9 | 31.6 | 1735 | 0.868/1.91 | 73.5 | 91
3X50+1X25 | 1.4/1.2 | 2 | 2.1 | 36.9 | 2414 | 0.641/1.2 | 91 | 112
3X70+1X35 | 1.4/1.4 | 2 | 2.2 | 40.7 | 2898 | 0.443/0.868 | 115.5 | 136.5
3X95+1X50 | 1.6/1.4 | 2 | 2.4 | 45.7 | 3582 | 0.32/0.641 | 143.5 | 164.5
3X120+1X70 | 1.6/1.4 | 2.5 | 2.5 | 51.1 | 4617 | 0.253/0.443 | 168 | 185.5
3X150+1X70 | 1.8/1.4 | 2.5 | 2.6 | 54.8 | 5243 | 0.206/0.443 | 189 | 210
3X185+1X95 | 2.0/1.6 | 2.5 | 2.8 | 60 | 6202 | 0.164/0.32 | 220.5 | 238
3X240+1X120 | 2.2/1.6 | 2.5 | 3 | 66.5 | 7425 | 0.125/0.253 | 262.5 | 276.5
3X300+1X150 | 2.4/1.8 | 3.15 | 3.2 | 77.7 | 8715 | 0.1/0.206 | 304.5 | 311.5
0.6/1kV-4+1 core aluminum conductor PVC insulated steel wire armored PVC sheathed power cable
Nominal cross sectional area | Insulation thickness | Steel Wire diameter | Sheath thickness | Approximate outer diameter | Approx. weight | Max.D.C resistance of conductor（20℃） | Current carrying capacity
mm2 | mm | mm | mm | mm | kg/km | Ω/km | In Air(A) | In Ground(A)
4X4+1X2.5 | 1.0/0.8 | 1.25 | 1.8 | 20.3 | 707 | 7.41/12.1 | 20.3 | 28
4X6+1X4 | 1.0/1.0 | 1.25 | 1.8 | 21.9 | 815 | 4.61/7.41 | 27.3 | 36.4
4X10+1X6 | 1.0/1.0 | 1.6 | 1.8 | 25.5 | 1147 | 3.08/4.61 | 35 | 46.2
4X16+1X10 | 1.0/1.0 | 1.6 | 1.8 | 28.6 | 1405 | 1.91/3.08 | 45.5 | 59.5
4X25+1X16 | 1.2/1.0 | 1.6 | 1.9 | 33 | 1803 | 1.2/1.91 | 60.9 | 77
4X35+1X16 | 1.2/1.0 | 2 | 2 | 35.4 | 2256 | 0.868/1.91 | 73.5 | 91
4X50+1X25 | 1.4/1.2 | 2 | 2.2 | 40.7 | 2854 | 0.641/1.2 | 91 | 112
4X70+1X35 | 1.4/1.4 | 2 | 2.3 | 44.7 | 3405 | 0.443/0.868 | 115.5 | 136.5
4X95+1X50 | 1.6/1.4 | 2.5 | 2.6 | 52.1 | 4800 | 0.32/0.641 | 143.5 | 164.5
4X120+1X70 | 1.6/1.4 | 2.5 | 2.7 | 56.2 | 5486 | 0.253/0.443 | 168 | 185.5
4X150+1X70 | 1.8/1.4 | 2.5 | 2.8 | 60.6 | 6223 | 0.206/0.443 | 189 | 210
4X185+1X95 | 2.0/1.6 | 2.5 | 3 | 66.8 | 7469 | 0.164/0.32 | 220.5 | 238
4X240+1X120 | 2.2/1.6 | 2.5 | 3.2 | 73.9 | 89662 | 0.125/0.253 | 262.5 | 276.5
4X300+1X150 | 2.4/1.8 | 3.15 | 3.5 | 82.5 | 11606 | 0.1/0.206 | 304.5 | 311.5
0.6/1kV-3+2 core aluminum conductor PVC insulated steel wire armored PVC sheathed power cable
Nominal cross sectional area | Insulation thickness | Steel Wire diameter | Sheath thickness | Approximate outer diameter | Approx. weight | Max.D.C resistance of conductor（20℃） | Current carrying capacity
mm2 | mm | mm | mm | mm | kg/km | Ω/km | In Air(A) | In Ground(A)
3X4+2X2.5 | 1.0/0.8 | 1.25 | 1.8 | 19.8 | 681 | 7.41/12.1 | 20.3 | 28
3X6+2X4 | 1.0/1.0 | 1.25 | 1.8 | 21.6 | 794 | 4.61/7.41 | 27.3 | 36.4
3X10+2X6 | 1.0/1.0 | 1.6 | 1.8 | 24.8 | 1103 | 3.08/4.61 | 35 | 46.2
3X16+2X10 | 1.0/1.0 | 1.6 | 1.8 | 28 | 1357 | 1.91/3.08 | 45.5 | 59.5
3X25+2X16 | 1.2/1.0 | 1.6 | 1.8 | 31.9 | 1709 | 1.2/1.91 | 60.9 | 77
3X35+2X16 | 1.2/1.0 | 1.6 | 1.9 | 33.1 | 1859 | 0.868/1.91 | 73.5 | 91
3X50+2X25 | 1.4/1.2 | 2 | 2.1 | 39.5 | 2752 | 0.641/1.2 | 91 | 112
3X70+2X35 | 1.4/1.4 | 2 | 2.3 | 42.8 | 3156 | 0.443/0.868 | 115.5 | 136.5
3X95+2X50 | 1.6/1.4 | 2.5 | 2.5 | 49.5 | 4381 | 0.32/0.641 | 143.5 | 164.5
3X120+2X70 | 1.6/1.4 | 2.5 | 2.6 | 54.2 | 5138 | 0.253/0.443 | 168 | 185.5
3X150+2X70 | 1.8/1.4 | 2.5 | 2.7 | 57.5 | 5711 | 0.206/0.443 | 189 | 210
3X185+2X95 | 2.0/1.6 | 2.5 | 2.9 | 63.8 | 6872 | 0.164/0.32 | 220.5 | 238
3X240+2X120 | 2.2/1.6 | 2.5 | 3.1 | 70.1 | 8158 | 0.125/0.253 | 262.5 | 276.5
3X300+2X150 | 2.4/1.8 | 3.15 | 3.4 | 78 | 10462 | 0.1/0.206 | 304.5 | 311.5